## Slide 1: Heat pumps and thermal energy storage
August Brækken, SINTEF Energy Research
12 September 2023

## Slide 2: What is a heat pump?
Moves heat from a region of lower temperature to a region of higher temperature
Utilises waste heat or heat from ambient
Used for heating and/or cooling of buildings or in industry
Only have to add electricity for compressor
evaporator
condenser
compressor
expansion valve
[1]

## Slide 3: Coefficient of Performance
evaporator
condenser
compressor
expansion valve
[1]

## Slide 4: Heat sources
Ambient air
Seawater
Ground
  Bedrock (boreholes)
  Soil
  Groundwater
Sewage (black water)
Grey water
Exhaust air from ventilation
Industry waste heat

## Slide 5: Working fluids
CFCs, HCFCs (previously)
HFCs (currently phased out)
HFOs
Natural working fluids:
  Hydrocarbons: propane, butane
  Ammonia
  CO2
  Water

## Slide 6: Natural working fluids
Hydrocarbons: propane, butane
  Highly flammable (A3)
Ammonia
  High performance
  High toxicity (B2L)
  Corrosive
CO2 (A1)
  Low critical temperature  transcritical cycle
  Useful for heating tap water
Water (A1)
  Used in high-temperature heat pumps
[2]

## Slide 7: Thermal energy storage
Load shifting:
  Moving energy use from high demand periods to low demand periods
Sensible heat – temperature change:
  Short-term: water tanks
  Long-term: boreholes (with heat pump)
Latent heat – phase change:
  Phase change material (PCM): ice, paraffins, salt hydrates
  High energy storage density

## Slide 8: Dairy – Tine Bergen
[3]
60 m3
130 m3
130 m3
130 m3

## Slide 9: Dairy – Tine Bergen
[4]
Summer
Winter
Total energy flows in MWh
[3]
COPs
  Ammonia chillers: 4.2
  Ammonia heat pumps: 5.3-5.4
  Hybrid heat pump: 5.7-5.9
  Combined COP: 4.1

## Slide 10: Dairy – Tine Trondheim
[5]
Propane-butane cascade heat pump
  Temperature lift >100 °C
  Average combined COP: 3.4
  Average heating COP: 2.5

## Slide 11: District heating – Leangen
[6]
Local heating network for new neighbourhood in Trondheim
Annual heating demand:
  12.1 GWh
Waste heat from ice skating rink:
  3 GWh
  30 °C or 35 °C
Low temperature (LT) vs. medium temperature (MT) heating network

## Slide 12: District heating – Leangen
[6]
Low temperature (LT) case:
  30 °C waste heat: 25% utilised
  35 °C waste heat: 79% utilised
Medium temperature (MT) case:
  30 °C waste heat: 90% utilised
  35 °C waste heat: 92% utilised
  Higher waste heat temperature reduced the electricity use for the heat pump

## Slide 13: References
[1] Jørn Stene, Basic Thermodynamics for the Heat Pump Cycle, Norwegian University of Science and Technology, 2021
[2] Jørn Stene, Working Fluids (Refrigerants) for The Heat Pump Cycle, Norwegian University of Science and Technology, 2021
[3] M. Ahrens, S. Foslie, O. Moen, M. Bantle, and T. Eikevik, "Integrated high temperature heat pumps and thermal storage tanks for combined heating and cooling in the industry," Applied Thermal Engineering, vol. 189, 2021, https://doi.org/10.1016/j.applthermaleng.2021.116731
[4] M. Ahrens et al., "Performance analysis of high temperature heat pumps and thermal energy storages for a dairy", 15th IIR-Gustav Lorentzen conference on Natural Refrigerants, Trondheim, Norway, 2022, https://doi.org/10.18462/iir.gl2022.0107
[5] C. Schlemminger, M. Bantle, S. Jenssen, and M. Dallai, "Industrial high temperature heat pump for simultaneous production of ice-water and process-heat", 15th IIR-Gustav Lorentzen Conference on Natural Refrigerants, Trondheim, Norway, 2022, https://doi.org/10.18462/iir.gl2022.0166
[6] H. Kauko, D. Rohde, and A. Hafner, "Local Heating Networks with Waste Heat Utilization: Low or Medium Temperature Supply?", Energies, 2020, https://doi.org/10.3390/en13040954
This work is supported by the EEA and Norway Grants